|  |  |  | TECHNICAL SPECIFICATION |  |  |  |  | N°: | I-PT-4880.00-7109-200-CZ1-001 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  | CLIENT: | LOG/TM/ON |  |  |  |  |  |  |  |  | sheet: |  | 1 of 25 |  |
|  |  |  | Job: | TP 25 – PRODUCT CARRIERS 15600 DWT |  |  |  |  |  |  |  |  | - |  |  |  |
|  |  |  | aREA: | PETROBRAS FLEET |  |  |  |  |  |  |  |  | IN-4880-23-001 |  |  |  |
|  |  |  | Title: | TECHNICAL PROPOSAL FOR SWITCHBOARDS |  |  |  |  |  |  |  |  | LOG/PL/EGE |  |  |  |
|  |  |  |  |  |  |  |  |  |  |  |  |  | INTERNAL |  |  |  |
|  |  |  | BUILDER: CONSORCIO ECOVIX / MACLAREN |  |  |  |  |  |  |  | CONTRACT NUMBER: 7000.0130000.25.2 |  |  |  |  |  |
|  |  |  | TECHNICAL RESPONSIBLE: marcelo delano |  |  | CREA NUMBER: 2006118561 |  |  |  |  | kongsberg number: N/A |  |  |  |  |  |
| index of revision |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| REV. | description and/or revised sheets |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 0 | original issue |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Rev. 0 |  |  | Rev. A |  | Rev. B |  |  | Rev. C |  | Rev. D |  | Rev. E |  |  |
| Date |  | 22/10/2025 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| EXECUtion |  | daniel laranjo |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| check |  | davi pegado |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| APproval |  | marcelo delano |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| IN ACCORDANCE WITH STANDARD PE-1TP-00365, the information contained in this document is transpetro property and may not be used for |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| purposes other than thosespecifically indicated herein. this form is part of petrobras’ n-381-rev.m. |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

1.	Revision History	4

2.	Comments to Quotation	5

2.1	Deviations	5

3.	Energy System description	6

3.1	Kongsberg AC Solution	6

3.2	System Topology	7

3.2.1 Power System Topology	7

3.2.2 Hight Voltage Shore Connection system (OPTION)	7

4.	Scope of Supply	8

4.1	Kongsberg Low Voltage Switchboards	8

4.1.1 General Specification	8

4.1.1.1 Recommended Swtchigear installation	8

4.1.2 General incomer W. digital Layer – ACB and touchscreen functions	8

4.1.3 General incomer W. digital Layer – HW instruments and  functions	9

4.1.4 General incomer W. digital Layer – Protection functions	10

4.1.5 Bus tie W. digital Layer – ACB and touchscreen functions	11

4.1.6 Bus tie W. digital Layer – HW instruments and functions	12

4.1.7 Bus tie W. digital Layer – protection functions	12

4.2	450V Main  Switchboards	13

4.2.1 General Specification	13

4.2.2 Mechanical  Specification	13

4.2.3 Electrical Specification	14

4.3	450V Emergency Switchboards	16

4.3.1 General Specification	16

4.3.2 Mechanical Specification	16

4.3.3 Electrical Specification	16

4.4	220V Main Switchboards	17

4.4.1 General Specification	17

4.4.2 Mechanical  Specification	17

4.4.3 Electrical Specification	17

4.5	220V Emergency Distribution Board	18

4.5.1 General Specification	18

4.5.2 Mechanical Specification	18

4.5.3 Electrical Specification	19

4.6	Main Transformes	19

4.6.1 General Specification	19

4.6.2 Electrical Specification	20

4.6.3 Mechanical Specification	20

4.7	Low Voltage Shore Connection Cabinet	21

4.7.1 General Specification	21

4.7.2 Mechanical Specification	21

4.7.3 Electrical Specification	21

4.8	Hight Voltage Shore Connection Switchboard (OPTION)	22

4.8.1 General Specification	22

4.8.2 Mechanical Specification	22

4.8.3 Electrical Specification	22

4.9	Hight Voltage Shore Connection Transformer (OPTION)	23

4.9.1 General Specification	23

4.9.2 Electrical Specification	23

4.9.3 Mechanical Specification	24

4.10	Electrical Studies	24

4.10.1 Deliverables	24

5.	Spare Parts	25

6.	Commissioning	25

7.	Training	25

Not included	25

8.	CLASS	25

9.	Factory Acceptance Tests	25

10.	Documentation	25

11.	List of Attachments	26

## Revision History

| Rev. | Date | Description of Change | By whom |
| --- | --- | --- | --- |
| 0 | Aug 23, 2024 | First issue | RMCF |
| 2 | Jun 02, 2025 | Updated according to Building specification (9) | ERO |
| 3 | Jun 19, 2025 | Updated according to Building specification (9) and after tech meetings with yard. Small cleaning and info. | LBR |
| 4 | July 2, 2025 | Updated class notation | LBR |
| 5 | Sept 16, 2025 | Updated voltage level, added future HVSC description | ERO |
| 6 | Sept 22, 2025 | Added system studies | ERO |
| 7 | Oct 09, 2025 | Added deviation list | ERO |

## Comments to Quotation

09.10.2025

Added a deviation list in chapter 2.1

22.09.2025

Added description of system studies that will be delivered.

16.09.2025

Updated voltage levels to 450V, 220V. Added description for HVSC system, not included in the delivery.

09.09.2025

Updated voltage levels to 450V/220V.

02.07.2025

Updated class notation.

### Deviations

| No. | Customer technical requirement | Description of Deviation |
| --- | --- | --- |
| 01 | The MSB shall be equipped with optical arc detection sensors to trip the busbar's power circuit breakers. | Not included, typically not used for this vessel type. Can be included on request, at additional cost. |
| 02 | The automatic and manual controls shall be located in the MSB synchronization column | Manual control of sync and load is performed in each generator panel via the HMI touch panel. |
| 03 | The front and rear doors of electrical panels shall be fitted with handrails made of insulating material along the entire length of the panel | This type of switchboard has rear mounted busbars, hence there are no doors on the rear side. |
| 04 | Power quality monitoring shall be included for the main busbars | Not included, typically not used for this vessel type. Can be included on request, at additional cost. |
| 05 | The switchboards shall be designed for free standing mounting on a common base frame. Each cubicle shall consist of a framework built up of zinc plated squared tubes | The frame of the switchboard is built up of painted steel profiles. |
| 06 | The main busbar should preferably be located at the top of the panel, without splices, silver plated at the contact points | The contact points are not silver plated. The switchboard uses a purpose specific paste at the connection points |
| 07 | The busbars shall be made of electrolytic copper, insulated (sheathed) and fitted with silver plated contacts/terminations. | Busbars are not sheathed; they are located in a separate busbar compartment in the rear part of the switchboard. |
| 08 | In front of panel shall be mounted control equipment for the generator breaker, etc.: | Manual control of sync and load is performed in each generator panel via the HMI touch panel. |
| 09 | Main bus instrument. Mimic diagram in front including: - Running indicator emergency diesel - Emergency switchboard supplied from emergency generator - Emergency switchboard supplied from main switchboard | There is no mimic diagram in one section, information is available from the relevant section. Overall mimic is available from PMS operator station. |

## Energy System description

### Kongsberg AC Solution

The AC Solution is an integrated power electric system in which the main power generation is carried out by means of synchronous AC generators connected directly to an AC switchboard.

The AC Solution comprises generators, switchgear, variable speed drives and motors for propulsion, all controlled by Kongsberg power- and energy management systems.

Integration between the different main elements of the power system is based on standardized interfaces developed through extensive operational experience, focusing on safety, efficiency and flexibility.

A high level of flexibility is achieved by utilizing the main elements of the power system in various combinations. Pre-defined power system modes can be defined to meet operational requirements in different vessel operating modes.

Power Management System functions are described in further detail in “Section 3 – Instrument

System”

### System Topology

### 3.2.1 Power System Topology

Electric power generation consists of three generator sets connected to a 450V main switchboard. The rated system frequency is 60Hz. Power is distributed to main consumers and transformers from the main switchboard.

A bus-tie breaker is installed and is normally closed. A low volage shore connection system is included, the connection is synchronized towards the generators for transfer of load without going through black-out.

Power is distributed from main switchboard to large consumer groups like HVAC and Cargo, and to smaller power consumers through transformers.

There are spare breakers for future installation of High voltage shore connection and shaft generator system in   the main switchboard.

An emergency generator connects to an emergency switchboard to power all consumers defined for emergency operation. Under normal operation conditions, the emergency switchboard is powered from the main switchboard.

### 3.2.2 Hight Voltage Shore Connection system (OPTION)

The high voltage shore connection system is designed to comply with IEC 80005-1, Annex F For tankers is applied for this application. See sketch below for general connection system. The sketch below illustrates the system topology.

## Scope of Supply

### Kongsberg Low Voltage Switchboards

### 4.1.1 General Specification

The low voltage switchgear and control gear assembly is designed by Kongsberg       Maritime. It’s a unique enclosure solution, where a range of different cubicles can be assembled based on few standard components, joined together. This gives high flexibility, and a robust design tailor made for the marine industry. The switchboard has been designed according to 61439-1/2 and IEC60092-302.

### 4.1.1.1 Recommended Swtchigear installation

Front: Minimum 1200 mm free space in front is required to have escape route with doors open. Side: Minimum 250 mm free space on each side to open door more than 90 degrees.

Rear: Minimum 500 mm free space to have access for easy installation and maintenance. Top: Minimum 100 mm and minimum 300 mm where ARC flaps on top are required.

Environment: Switchgears must be placed in clean and well-ventilated locations. Cable entry: Bottom.

### 4.1.2 General incomer W. digital Layer – ACB and touchscreen functions

| Included is Kongsberg K-Power Digital Layer with fast measurement, protection, and functions. The plug-and-play interface to K-Chief PMS/EMS is done by Modbus TCP. Therefore, no additional transducers are installed or required. The air circuit breaker(s) (ACB) can be operated locally or remotely. |  |  |
| --- | --- | --- |
| Included as described in the Switchgear incomer | Functions: - Breaker Close / Open - Breaker Synchronize - Auto - Semi Auto - Prime Mover - Start / Stop - Speed Increase - Speed Decrease | Generator(s) incomer local breaker display (LBD) |

|  | Measurement/alarms: - Gen & Bus Voltage - Gen & Bus Freq. - Current - Power - Power factor - Status Indication - Instrument Indication - Alarm Acknowledge - Trip Reset | Generator(s) incomer on the local breaker display (LBD) |
| --- | --- | --- |

### 4.1.3 General incomer W. digital Layer – HW instruments and  functions

| Item | Qty | Description | Scale | Accuracy | HW components |
| --- | --- | --- | --- | --- | --- |
| 1 | 3 | Ampere meter | 130 % of rated current | 2.5 % or higher |  |
| 2 | 1 | Voltmeter w. phase selector switch (for the incomer and busbar) | 120 % of nominal voltage | 2.5 % or higher |  |
| 3 | 1 | Frequency meter for the incomer and busbar) | 8 % above and below nominal frequency | 2.5 % or higher |  |
| 4 | 1 | Active power meter (kW) | 130 % of rated current |  |  |
| 5 | 1 | Local/remote selector switch |  |  |  |

### 4.1.4 General incomer W. digital Layer – Protection functions

| The local synchronizing and protection (LSP) unit is a highly configurable controller designed for marine use. The controller contains the functions required to protect and control a generator and its breaker or bus tie breakers. Each controller includes processors and high-speed internal communication with fast protection. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ANSI code | IEC | Description | Latch | IAS alarms | Circuit breaker trip | AVR de-excitation trip | Protection |
| 27 | U<, U<< | Under-voltage |  | X | X |  | Voltage |
| 32 | P>, P>> | Overload |  | X1 |  |  | Power |
| 32R | P<, P<< | Reverse power |  | X | X |  | Power |
| 40O | Q>, Q>> | Reactive power export |  | X |  |  | AVR |
| 40U | Q<, Q<< | Reactive power import |  | X |  |  | AVR |
| 50TD | 3I>, 3I>> | Overcurrent |  | X | X |  | Current |
| 50/50TD | 3I>>> | Fast overcurrent | X |  | X | X | Current |
| 50BF |  | Breaker failure | X | X | X |  | Breaker |
| 51 | It> | Inverse time overcurrent | X | X | X |  | Current |
| 59 | U>, U>> | Overvoltage |  | X | X2 |  | Voltage |
| 67 | I0φ | Directional overcurrent | X | X | X3 |  | Current |
| 81U | f<, f<< | Under-frequency |  | X |  |  | Frequency |
| 81O | f>, f>> | Over-frequency |  | X |  |  | Frequency |
| 87G | Id>> | Differential protection | X | x | X | X | ≥1500 kVA (DNV |
| 1 Preferential trip output on the LSP, overload protection 1 and 2 as the source. Need to implement a DO in the LSP. 2 The generator must have a time delay due to coordination/selectivity and the bus tie to have the first trip. |  |  |  |  |  |  |  |

### 4.1.5 Bus tie W. digital Layer – ACB and touchscreen functions

| Included is Kongsberg K-Power Digital Layer with fast measurement, protection, and functions. The plug-and-play interface to K-Chief PMS/EMS is done by Modbus TCP. Therefore, no additional transducers are installed or needed. Air circuit breaker(s) (ACB) can be operated locally or remotely. |  |  |
| --- | --- | --- |
| Included as described in the Switchgear incomer and feeders chapter. | Functions: - Breaker Close / Open - Breaker Synch check | Bus tie local breaker display (LBD) |
|  | Measurement/alarms: - Bus 1 & Bus 2 Voltage - Bus 1 & Bus 2 Freq. - Power - Power factor - Status Indication - Instrument Indication - Alarm Acknowledge - Trip Reset | Generator(s) incomer local breaker display (LBD) |

### 4.1.6 Bus tie W. digital Layer – HW instruments and functions

| Item | Qty | Description | Scale | Accuracy | HW components |
| --- | --- | --- | --- | --- | --- |
| 1 | 0 |  |  |  |  |
| 2 | 1 | Voltmeter w. phase | 120 % of | 2.5 % or |  |
|  |  | selector switch | nominal | higher |  |
|  |  | (busbar 1 and | voltage |  |  |
|  |  | busbar 2) |  |  |  |
| 3 | 1 | Frequency meter | 8 % above | 2.5 % or |  |
|  |  | for incomer and | and below | higher |  |
|  |  | busbar | nominal |  |  |
|  |  |  | frequency |  |  |
| 4 | 1 | Local/remote |  |  |  |
|  |  | selector switch |  |  |  |
| 5 | 2 | Insulation guard |  |  |  |
|  |  | (one on each |  |  |  |
|  |  | busbar) |  |  |  |

### 4.1.7 Bus tie W. digital Layer – protection functions

| The local synchronizing and protection (LSP) unit is a highly configurable controller designed for marine use. The controller contains the functions required to protect and control a generator and its breaker or bus-tie breakers. Each controller includes processors and high-speed internal communication with fast protection. Alternatively, the protection may be a Micrologic that is integrated into the ACB. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ANSI code | IEC | Description | Latch | IAS alarms | Circuit breaker trip | AVR de-excitation trip | Protection |
| 27 | U<, U<< | Under-voltage |  | X |  |  | Voltage |
| 32 | P>, P>> | Overload |  |  |  |  | Power |
| 32R | P<, P<< | Reverse power |  |  |  |  | Power |
| 40O | Q>, Q>> | Reactive power export |  |  |  |  | AVR |
| 40U | Q<, Q<< | Reactive power import |  |  |  |  | AVR |
| 50TD | 3I>, 3I>> | Overcurrent |  | X | X |  | Current |
| 50/50TD | 3I>>> | Fast overcurrent | X |  | X |  | Current |
| 50BF |  | Breaker failure | X | X | X |  | Breaker |
| 51 | It> | Inverse time overcurrent | X | X | X |  | Current |
| 59 | U>, U>> | Overvoltage |  | X | X2 |  | Voltage |
| 67 | I0φ | Directional overcurrent |  |  |  |  | Current |
| 81U | f<, f<< | Under-frequency |  | X |  |  | Frequency |
| 81O | f>, f>> | Over-frequency |  | X |  |  | Frequency |
| 87G | Id>> | Differential protection |  |  |  |  | Current |
| 1 Preferential trip output on the LSP, overload protection 1 and 2 as the source. Must implement a DO in the LSP. 2 The generator must have a time delay due to coordination/selectivity and the bus tie to have the first trip. |  |  |  |  |  |  |  |

### 450V Main  Switchboards

### 4.2.1 General Specification

Quantity	1

### 4.2.2 Mechanical  Specification

Main dimensions

Estimated Size (W x D x H)	6250 x 600 x 2200 mm

Estimated Weight	4924 kg

Cooling system

Cooling Method	Air

Estimated Heat Load to Air	6017 W

Terminals and protection

Ingress Protection	P23

Access	Front & rear

Cable Entry	Bottom

Painting	RAL9005 (Jet Black) / RAL9006 (White Aluminum)

Environmental conditions

Air temperature range (room)	0 – 45°C

.	condensation, splash water and ice formation not permitted

Construction standards

LV Air circuit breakers (ACB). Form according to	EC 61439

Withdrawable	Form 3a

LV Molded-case circuit breakers (MCCB). Form according to	EC 61439

Fixed/ Plug-In	Form 1

### 4.2.3 Electrical Specification

Bus-bar nominal voltage	V

Bus-bar nominal frequency	60 Hz

Bus-bar nominal rating	2865 A

Short circuit level (Icw)	50 kA, 1 s.

Distribution system	IT

+01 Feeders (MCCB)

TYPE	Plug-In

Feeder NS 800 A	0

Feeder NSX 630 A	0

Feeder NSX 400 A	4

Feeder NSX 250 A	4

Feeder NSX 160 A	0

Feeder NSX 100 A	2

Feeder NSXm 160 A	0

Feeder NSXm 63 A	0

+02 Feeder (ACB)

Name	CARGO1

Generator Rated Active Power	600 kVA

ACB Rated Current	800 A

MicroLogic	5

+03 HVSC Incomer (ACB)

Name	HVSC

Generator Apparent Power	1850 kVA

ACB Rated Current	2900 A

LBD	Yes

LSP	Yes

+04 Shaft Generator Incomer (ACB)

Name	SG

Generator Apparent Power	688 kVA

ACB Rated Current	1000 A

Form Factor 4b Selected	No

LBD	Yes

LSP	Yes

+05 Generator Incomer (ACB)

Name	G3

Generator Apparent Power	938 kVA

ACB Rated Current	1250 A

LBD	Yes

LSP	Yes

+06 Bus-Tie (ACB)

Name	Bus-Tie

Rated Apparent Power	1750 kVA

ACB Rated Current	2900 A

MicroLogic Included	5

LBD	Yes

LSP	Yes

+07 Generator Incomer (ACB)

Name	G2

Generator Apparent Power	938 kVA

ACB Rated Current	1250 A

LBD	Yes

LSP	Yes

+08 Generator Incomer (ACB)

Name	G1

Generator Apparent Power	938 kVA

ACB Rated Current	1250 A

LBD	Yes

LSP	Yes

+09 Shore Power Incomer (ACB)

Name	LVSC

Generator Apparent Power	380 kVA

ACB Rated Current	630 A

Form Factor 4b Selected	No

LBD	Yes

LSP	Yes

+10 Feeder (ACB)

Name	CARGO2

Generator Rated Active Power	600 kVA

ACB Rated Current	800 A

MicroLogic	5

+11 Feeder (ACB)

Name	EMG

Generator Rated Active Power	250 kVA

ACB Rated Current	630 A

MicroLogic	5

+12 Feeders (MCCB)

TYPE	Plug-In

Feeder NS 800 A	0

Feeder NSX 630 A	0

Feeder NSX 400 A	4

Feeder NSX 250 A	4

Feeder NSX 160 A	0

Feeder NSX 100 A	2

Feeder NSXm 160 A	0

Feeder NSXm 63 A	0

### 450V Emergency Switchboards

### 4.3.1 General Specification

Quantity	1

### 4.3.2 Mechanical Specification

Main dimensions

Estimated Size (W x D x H)	2050 x 600 x 2200 mm

Estimated Weight	1830 kg

Cooling system

Cooling Method	Air

Estimated Heat Load to Air	2596 W

Terminals and protection

Ingress Protection	P23

Access	Front & rear

Cable Entry	Bottom

Painting	RAL9005 (Jet Black) / RAL9006 (White Aluminum)

Environmental conditions

Air temperature range (room)	0 – 45°C

.	condensation, splash water and ice formation not permitted

Construction standards

LV Air circuit breakers (ACB). Form according to	EC 61439

Withdrawable	Form 3a

LV Molded-case circuit breakers (MCCB). Form according to	EC 61439

Fixed/ Plug-In	Form 1

### 4.3.3 Electrical Specification

Bus-bar nominal voltage	V

Bus-bar nominal frequency	60 Hz

Bus-bar nominal rating	950 A

Short circuit level (Icw)	42 kA, 1 s.

Distribution system	IT

+01Generator Incomer (ACB)

Name	EG

Generator Apparent Power	kVA

ACB Rated Current	630 A

Form Factor 4b Selected	No

LBD	No

LSP	No

+02 Incomer (ACB)

Name	MSB

Generator Apparent Power	250 kVA

ACB Rated Current	630 A

Form Factor 4b Selected	No

LSP	No

+03 Feeders (MCCB)

TYPE	PlugIn

Feeder NS 800 A	0

Feeder NSX 630 A	4

Feeder NSX 400 A	0

Feeder NSX 250 A	12

Feeder NSX 160 A	0

Feeder NSX 100 A	4

### 220V Main Switchboards

### 4.4.1 General Specification

Quantity	1

### 4.4.2 Mechanical  Specification

Main dimensions

Estimated Size (W x D x H)	2850 x 600 x 2200 mm

Estimated Weight	1575 kg

Cooling system

Cooling Method	Air

Estimated Heat Load to Air	2356 W

Terminals and protection

Ingress Protection	P23

Access	Front & rear

Cable Entry	Bottom

Painting	RAL9005 (Jet Black) / RAL9006 (White Aluminum)

Environmental conditions

Air temperature range (room)	0 – 45°C

.	condensation, splash water and ice formation not permitted

Construction standards

LV Air circuit breakers (ACB). Form according to	EC 61439

Withdrawable	Form 3a

LV Molded-case circuit breakers (MCCB). Form according to	EC 61439

Fixed/ Plug-In	Form 1

### 4.4.3 Electrical Specification

Bus-bar nominal voltage	V

Bus-bar nominal frequency	60 Hz

Bus-bar nominal rating	950 A

Short circuit level (Icw)	42 kA, 1 s.

Distribution system	IT

+01 Feeders (MCCB)

TYPE	Fixed

Feeder NS 800 A	0

Feeder NSX 630 A	2

Feeder NSX 400 A	0

Feeder NSX 250 A	6

Feeder NSX 160 A	0

Feeder NSX 100 A	2

Feeder NSXm 160 A	0

Feeder NSXm 63 A	0

+02 Transformer Incomer (ACB)

Name	T1

Generator Apparent Power	250 kVA

ACB Rated Current	630 A

+03 Tranaformer Incomer (ACB)

Name	T2

Generator Apparent Power	250 kVA

ACB Rated Current	630 A

+04 Bus-Tie (ACB)

Name	BT

Rated Apparent Power	250 kVA

ACB Rated Current	800 A

+05 Feeders (MCCB)

TYPE	Fixed

Feeder NS 800 A	0

Feeder NSX 630 A	2

Feeder NSX 400 A	0

Feeder NSX 250 A	6

Feeder NSX 160 A	0

Feeder NSX 100 A	2

Feeder NSXm 160 A	0

Feeder NSXm 63 A	0

### 220V Emergency Distribution Board

### 4.5.1 General Specification

Quantity	1

### 4.5.2 Mechanical Specification

Main dimensions

Estimated Size (W x D x H)	1450 x 600 x 2200 mm

Estimated Weight	768 kg

Cooling system

Cooling Method	Air

Estimated Heat Load to Air	1623 W

Terminals and protection

Ingress Protection	P23

Access	Front & rear

Cable Entry	Bottom

Painting	RAL9005 (Jet Black) / RAL9006 (White Aluminum)

Environmental conditions

Air temperature range (room)	0 – 45°C

.	condensation, splash water and ice formation not permitted

Construction standards

LV Air circuit breakers (ACB). Form according to	EC 61439

Withdrawable	Form 3a

LV Molded-case circuit breakers (MCCB). Form according to	EC 61439

Fixed/ Plug-In	Form 1

### 4.5.3 Electrical Specification

Bus-bar nominal voltage	V

Bus-bar nominal frequency	60 Hz

Bus-bar nominal rating	950 A

Short circuit level (Icw)	42 kA, 1 s.

Distribution system	IT

+01Feeders (MCCB)

TYPE	Fixed

Feeder NS 800 A	0

Feeder NSX 630 A	5

Feeder NSX 400 A	0

Feeder NSX 250 A	11

Feeder NSX 160 A	0

Feeder NSX 100 A	4

Feeder NSXm 160 A	0

Feeder NSXm 63 A	0

### Main Transformes

### 4.6.1 General Specification

Qty	2

Application / Environment	Distribution

Transformer Type	Dry transformer

### 4.6.2 Electrical Specification

Rated Apparent power	250 kVA

Duty	Continuous

Load type	Distribution THD 8 %

Number of phases	3

Connection	Dy11

Primary voltage	V

Secondary voltage	V

Rated frequency	60 Hz

Insulation class	H

Temperature rise class	F

Cu screen	Not Included

Pre-magnetization	Included

### 4.6.3 Mechanical Specification

Ingress Protection	P23

Cable entry primary side	Bottom

Cable entry secondary side	Bottom

Power cable terminals (No. of cables)	Manufacturer’s standard

Windings	Aluminium

Enclosure	Steel

Terminals	Cu

Environment / Climatic / Fire class	E1 / C1 / F0

Colour	RAL 7035

MCT frame	Included

Cooling system

Cooling method	AN

Estimated heat load to air	5.0kW

Main dimensions

Estimated Size (W x D x H)	1200 x 1000 x 1300 mm

Estimated Weight	900 kg

Terminals and protection

Winding temperature monitoring .................................................................................... PT-100

Environmental conditions

Air temperature range (room)	0 – 45 °C

### Low Voltage Shore Connection Cabinet

The CSCC panel is a conventional shore connection panel with a circuit breaker and connection point for shore      power cables. The cable entry is through a hatch and the cables are connected by lugs and bolts.

### 4.7.1 General Specification

Qty	1

Panel type	CSCC4-8V

### 4.7.2 Mechanical Specification

Estimated Size TBC (W x D x H)	760 x 300 x 760 mm

Ingress Protection	P 44

Cable entry	Hatch

### 4.7.3 Electrical Specification

Rated Voltage	V

Rated Frequency	60 Hz

Rated Current	500A

Number of phases	3 ph. + 1 P.E

### Hight Voltage Shore Connection Switchboard (OPTION)

### 4.8.1 General Specification

Quantity	1 pcs.

Type	Kongsberg High Voltage Switchboard

### 4.8.2 Mechanical Specification

Main dimensions

Estimated Size (W x D x H)	1280 x 1320 x 2750 mm

Estimated Weight	 1660 kg

Cooling system

Cooling Method	Air Natural

Estimated Heat Load to Air	0.5 kW

Air flow	TBC m3/h

Terminals and protection

Ingress Protection	IP 42 (Open bottom)

Access Requirement	Front & Back

Cable Entry	Bottom

Painting	RAL9005 (Jet Black) / RAL9006 (White Aluminum)

Environmental conditions

Air temperature range (room)	0 – 45°C

Degree of pollution...................................................................................... 2 (IEC/EN 61800-5-1)

Air humidity	... 5-95 %rh

.	Condensation, splash water and ice formation not permitted

Air pressure equivalence	≤ 2000 masl

Displacement limit (vibration)	1.0 mm at 2 - 13.2 Hz

Acceleration limit (vibration) ................................................................... 0.7 g at >13.2	100 Hz

Radio interference	special power distribution zone (IEC 60533)

Construction standards

Design	EC 62271-200

Vacuum circuit breakers (VCB)	EC62271-100

Withdrawable	Form Factor 3b

### 4.8.3 Electrical Specification

Bus nominal voltage	kV

Bus rated voltage	kV

Bus nominal frequency	60 Hz

Bus nominal current	1250 A

Short circuit level (Icw)	25 kA, 1 s.

Distribution system	IT

+01 Auxiliary Panel (Riser panel)

Name	BUSMEASURE

VCB Rated Current	N.A

Protection Device	N.A

Grounding Switch	Yes (Bus Grounding)

+02 Switchboard Feeder

Name	MS1

VCB Rated Current	630A

Protection Device	P3F30

Grounding Switch	Yes (Cable Side)

### Hight Voltage Shore Connection Transformer (OPTION)

### 4.9.1 General Specification

Qty	1

Application / Environment	Shore Connection

Transformer Type	Dry transformer

### 4.9.2 Electrical Specification

Rated Apparent power	1850 kVA

Duty	Continuous

Load type	Distribution THD 8 %

Number of phases	3

Connection	Dy11

Primary voltage ..................................................................................................................6600 V

Secondary voltage	V

Rated frequency	60 Hz

Insulation class	H

Temperature rise class	F

Cu screen	Not Included

Pre-magnetization	Included

### 4.9.3 Mechanical Specification

Ingress Protection	P44

Cable entry primary side	Bottom

Cable entry secondary side	Bottom

Power cable terminals (No. of cables)	Manufacturer’s standard

Windings	Aluminium

Enclosure	Steel

Terminals	Cu

Environment / Climatic / Fire class	E1 / C1 / F0

Colour	RAL 7035

MCT frame	Included

Cooling system

Cooling method	AFWF

Estimated heat load to air	TBC

Coolant inlet temperature range (ship side)	38 °C

Secondary Cooling	Freshwater w/glycol

Cooling fan	450 V, 60 Hz

Main dimensions

Estimated Size (W x D x H)	2700 x 1800 x 2000 mm

Estimated Weight	5000 kg

Terminals and protection

Winding temperature monitoring .................................................................................... PT-100

Leakage detector	Yes

Environmental conditions

Air temperature range (room)	0 – 45 °C

### Electrical Studies

A model of the electrical system is made based on information about loads and power supply. The vessel load list is needed as input to the model.

The results of the simulations will be delivered as documents according to the Supplier master document lists (SMDL). Information from client related to systems and items outside of

Kongsberg’s scope of supply must be in hand within due time to perform the analysis and deliver the documents according to the documentation plan.

### 4.10.1 Deliverables

The Following documents will be supplied:

- Short Circuit Calculation (for defined operational modes)

- Voltage-drop analysis

- Protection coordination (for KM delivered switchboards)

- Load flow study

An arc flash test of Kongsberg Low Voltage switchboard has been perfomed, test report will be submitted.

## Spare Parts

Operational spare parts for two years are not required but can be added upon request.

## Commissioning

Ref. to Kongsberg Maritime General Terms and Conditions for Commissioning Services

Commissioning:

40 days (at 10 hours per day)

Waiting time is not included and will be invoiced. Living and lodging           expenses for the period are included

Additional assistance:

Additional assistance will be charged in accordance with Kongsberg standard rates

## Training

## Not included

## CLASS

The equipment and system will be delivered in accordance with BV (Bureau Veritas)

The following notations will be applicable:

I, OIL TANKER, ESP, METHANOLFUEL-PREPARED (S, T, H, P, ME-DF, AE, B), CPS(WBT), COMF-VIB 3, COMF-NOISE 3, AUT-UMS, AVM, SYS-NEQ-1, CARGOCONTROL, LI-S3, VCS-TRANSFER, IG, SPM, CYBER SECURE, SMART (EnE2), ETA, BWT, CLEANSHIP, SOX-x%, GREENPASSPORT, INWATERSURVEY, MON-SHAFT, ALM

## Factory Acceptance Tests

For equipment with project specific certification requirement a standard workshop test in the presence of class surveyor and customer (if required) will be performed.

The following equipment is subject to project specific certification:

- 450V Main Switchboard

- 450/220V Emergency Switchboard

- 220V Main Switchboard

- Main Transformers

For equipment without project specific certification requirement a standard workshop test will be performed or following suppliers QA system

## Documentation

A project specific SMDL (Supplier Master Document List) will be provided soon after project is established. It will contain all documents related to the products and systems specified in this technical quotation. The SMDL also contains information about when each document will be ready, and who shall receive it.

## List of Attachments

Main Single Line Diagram

450V Main Switchboard – General Arrangement 220V Main Switchboard – General Arrangement

450V/220V Emergency Switchboard – General Arrangement